## Altres_criteris_taulat
TRACT | Capacitat_min | Capacitac_max | Consum_energetic_mitja | FeCl3 | NaOCl | Acid_citric | NaOH | HCl | H2O2 | Carbo_actiu | HC | HH | Espai_ocupat | OPEX | CAPEX_min | CAPEX_max | CAPEX_min | CAPEX_max | Temps_estabilitzacio | REF.
| m3/d | m3/d | kWh/m3 | g/m3 | g/m3 | g/m3 | g/m3 | g/m3 | g/m3 | g/m3 | kg CO2 eq./m3 | L eq./m3 | m2/m3/d | €/m3 | €/m3/d | €/m3/d | €/m3 | €/m3 | d
FS | 0 | 2000 | 0.4 | [7 empty] | 0.0964 | 0.65482 | 0.025 | 0.07 | 12.5 | 15 | 0.0011416 | 0.0013699 | 1 | [9]
FS | 2001 | 10000 | 0.3 | [7 empty] | 0.0723 | 0.49111 | 0.021 | 0.06 | 10 | 12.5 | 0.00091324 | 0.0011416 | 1 | [9]
FS | 10001 | 50000 | 0.2 | [7 empty] | 0.0482 | 0.32741 | 0.018 | 0.05 | 7.5 | 10 | 0.00068493 | 0.00091324 | 1 | [9]
FS | 50001 | 1000000 | 0.1 | [7 empty] | 0.0241 | 0.1637 | 0.015 | 0.04 | 5 | 7.5 | 0.00045662 | 0.00068493 | 1 | [9]
BFS | 0 | 2000 | 0.4 | [7 empty] | 0.0964 | 0.65482 | 0.025 | 0.077 | 13.75 | 16.5 | 0.0012557 | 0.0015068 | 30 | Estimació a partir del cost del FS de [9]
BFS | 2001 | 10000 | 0.3 | [7 empty] | 0.0723 | 0.49111 | 0.021 | 0.066 | 11 | 13.75 | 0.0010046 | 0.0012557 | 30 | Estimació a partir del cost del FS de [9]
BFS | 10001 | 50000 | 0.2 | [7 empty] | 0.0482 | 0.32741 | 0.018 | 0.055 | 8.25 | 11 | 0.00075342 | 0.0010046 | 30 | Estimació a partir del cost del FS de [9]
BFS | 50001 | 1000000 | 0.1 | [7 empty] | 0.0241 | 0.1637 | 0.015 | 0.044 | 5.5 | 8.25 | 0.00050228 | 0.00075342 | 30 | Estimació a partir del cost del FS de [9]
CAB | 0 | 2000 | 0.4 | [6 empty] | 30 | 0.15381 | 0.94423 | 0.025 | 0.32 | 412.5 | 605 | 0.037671 | 0.055251 | 30 | Estimació a partir del cost de [41]
CAB | 2001 | 10000 | 0.3 | [6 empty] | 30 | 0.12971 | 0.78052 | 0.021 | 0.26 | 275 | 412.5 | 0.025114 | 0.037671 | 30 | Estimació a partir del cost de [41]
CAB | 10001 | 50000 | 0.2 | [6 empty] | 30 | 0.10561 | 0.61682 | 0.018 | 0.189 | 192.5 | 275 | 0.01758 | 0.025114 | 30 | Estimació a partir del cost de [41]
CAB | 50001 | 1000000 | 0.1 | [6 empty] | 30 | 0.08151 | 0.45311 | 0.015 | 0.132 | 165 | 192.5 | 0.015068 | 0.01758 | 30 | Estimació a partir del cost de [41]
FQ_D | 0 | 2000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.019 | 0.066 | 9.5 | 14 | 0.00086758 | 0.0012785 | 1 | [41]
FQ_D | 2001 | 10000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.017 | 0.066 | 7.7 | 13.4 | 0.0007032 | 0.0012237 | 1 | [41]
FQ_D | 10001 | 50000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.014 | 0.056 | 4.9 | 7.7 | 0.00044749 | 0.0007032 | 1 | [41]
FQ_D | 50001 | 1000000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.012 | 0.054 | 4.9 | 5.1 | 0.00044749 | 0.00046575 | 1 | [41]
EDI | 0 | 2000 | 1.5 |  |  |  |  | 0.0003 |  |  | 0.3615 | 2.4556 | 0.095 | 0.4 | 350 | 400 | 0.031963 | 0.03653 | 1 | [9]
EDI | 2001 | 10000 | 1.3 |  |  |  |  | 0.0003 |  |  | 0.3133 | 2.1282 | 0.082 | 0.3 | 300 | 350 | 0.027397 | 0.031963 | 1 | [9]
EDI | 10001 | 50000 | 1.1 |  |  |  |  | 0.0003 |  |  | 0.2651 | 1.8007 | 0.07 | 0.25 | 225 | 300 | 0.020548 | 0.027397 | 1 | [9]
EDI | 50001 | 1000000 | 0.8 |  |  |  |  | 0.0003 |  |  | 0.1928 | 1.3096 | 0.065 | 0.2 | 200 | 225 | 0.018265 | 0.020548 | 1 | [9]
CAP_CAG | 0 | 2000 | 0.4 | [6 empty] | 30 | 0.15381 | 0.94423 | 0.025 | 0.32 | 375 | 550 | 0.034247 | 0.050228 | 1 | [41]
CAP_CAG | 2001 | 10000 | 0.3 | [6 empty] | 30 | 0.12971 | 0.78052 | 0.021 | 0.26 | 250 | 375 | 0.022831 | 0.034247 | 1 | [41]
CAP_CAG | 10001 | 50000 | 0.2 | [6 empty] | 30 | 0.10561 | 0.61682 | 0.018 | 0.189 | 175 | 250 | 0.015982 | 0.022831 | 1 | [41]
CAP_CAG | 50001 | 1000000 | 0.1 | [6 empty] | 30 | 0.08151 | 0.45311 | 0.015 | 0.132 | 150 | 175 | 0.013699 | 0.015982 | 1 | [41]
UV_H2O2 | 0 | 2000 | 0.75 | [5 empty] | 9.9 |  | 0.19264 | 1.2858 | 0.068 | 0.6 | 250 | 300 | 0.022831 | 0.027397 | 0 | [41][42]
UV_H2O2 | 2001 | 10000 | 0.5 | [5 empty] | 9.9 |  | 0.13239 | 0.8765 | 0.059 | 0.5 | 200 | 225 | 0.018265 | 0.020548 | 0 | [41][42]
UV_H2O2 | 10001 | 50000 | 0.3 | [5 empty] | 9.9 |  | 0.08419 | 0.54909 | 0.051 | 0.45 | 150 | 175 | 0.013699 | 0.015982 | 0 | [41][42]
UV_H2O2 | 50001 | 1000000 | 0.17 | [5 empty] | 9.9 |  | 0.05286 | 0.33628 | 0.0422 | 0.4 | 100 | 135 | 0.0091324 | 0.012329 | 0 | [41][42]
O3 | 0 | 2000 | nd | [7 empty] | nd | nd | 0.068 | 0.6 | 250 | 300 | 0.022831 | 0.027397 | 0
O3 | 2001 | 10000 | nd | [7 empty] | nd | nd | 0.059 | 0.5 | 200 | 225 | 0.018265 | 0.020548 | 0
O3 | 10001 | 50000 | nd | [7 empty] | nd | nd | 0.051 | 0.45 | 150 | 175 | 0.013699 | 0.015982 | 0
O3 | 50001 | 1000000 | nd | [7 empty] | nd | nd | 0.0422 | 0.4 | 100 | 135 | 0.0091324 | 0.012329 | 0
DES | 0 | 2000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0015 | 0.002 | 12.5 | 15 | 0.0011416 | 0.0013699 | 0 | [9]
DES | 2001 | 10000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0013 | 0.002 | 10 | 12.5 | 0.00091324 | 0.0011416 | 0 | [9]
DES | 10001 | 50000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0011 | 0.001 | 7.5 | 10 | 0.00068493 | 0.00091324 | 0 | [9]
DES | 50001 | 1000000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.00093 | 0.001 | 5 | 7.5 | 0.00045662 | 0.00068493 | 0 | [9]
BRM | 0 | 2000 | 1.2 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.39972 | 9.208 | 0.9 | 1.1 | 1600 | 3000 | 0.14612 | 0.27397 | 30 | [47]
BRM | 2001 | 10000 | 0.7 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.27922 | 8.3895 | 0.6 | 0.5 | 1000 | 1600 | 0.091324 | 0.14612 | 30 | [47]
BRM | 10001 | 50000 | 0.6 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.25512 | 8.2258 | 0.5 | 0.4 | 800 | 1000 | 0.073059 | 0.091324 | 30 | [47]
BRM | 50001 | 1000000 | 0.55 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.24307 | 8.1439 | 0.4 | 0.2 | 600 | 800 | 0.054795 | 0.073059 | 30 | [47]
MF/UF | 0 | 2000 | 0.6 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.17285 | 3.4751 | 0.069 | 0.85 | 1400 | 1800 | 0.12785 | 0.16438 | 0 | [41]. LIFE WIRE
MF/UF | 2001 | 10000 | 0.5 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.14875 | 3.3113 | 0.063 | 0.56 | 800 | 1400 | 0.073059 | 0.12785 | 0 | [41]. LIFE WIRE
MF/UF | 10001 | 50000 | 0.3 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.10055 | 2.9839 | 0.054 | 0.32 | 450 | 800 | 0.041096 | 0.073059 | 0 | [41]. LIFE WIRE
MF/UF | 50001 | 1000000 | 0.1 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.05235 | 2.6565 | 0.045 | 0.13 | 350 | 450 | 0.031963 | 0.041096 | 0 | [41]. LIFE WIRE
OI | 0 | 2000 | 3.5 |  |  |  | 0.8 | 0.0003 |  |  | 0.84527 | 5.7523 | 0.092 | 0.24 | 500 | 650 | 0.045662 | 0.059361 | 1 | [41]. LIFE WIRE
OI | 2001 | 10000 | 2 |  |  |  | 0.8 | 0.0003 |  |  | 0.48377 | 3.2967 | 0.081 | 0.2 | 350 | 500 | 0.031963 | 0.045662 | 1 | [41]. LIFE WIRE
OI | 10001 | 50000 | 1.5 |  |  |  | 0.8 | 0.0003 |  |  | 0.36327 | 2.4782 | 0.069 | 0.18 | 275 | 350 | 0.025114 | 0.031963 | 1 | [41]. LIFE WIRE
OI | 50001 | 1000000 | 1 |  |  |  | 0.8 | 0.0003 |  |  | 0.24277 | 1.6597 | 0.055 | 0.17 | 250 | 275 | 0.022831 | 0.025114 | 1 | [41]. LIFE WIRE

## Temps_operacio
Assumpcions
Temps operació
anys
Planta general | 30

## Altres_Caract
TRAC. | Capacitat_min[m3/dia] | Capacitac_max[m3/dia] | Consum_energetic_mitg[kWh/m3] | FeCl3(g/m3) | NaOCl(g/m3) | Acid Citric(g/m3) | NaOH(g/m3) | HCl(g/m3) | H2O2(g/m3) | Carbo_actiu(g/m3) | HC[kg CO2 eq./m3] | HH[L eq./m3] | Espai_ocupat[m2/m3/d] | OPEX[€/m3] | CAPEX_MIN[€/m3/día] | CAPEX_MAX[€/m3/día] | Temps_estabilitzacio(d) | REF.
FS | 0 | 2000 | 0.4 | [7 empty] | 0.0964 | 0.65482 | 0.025 | 0.07 | 12.5 | 15 | 1 | [9]
FS | 2001 | 10000 | 0.3 | [7 empty] | 0.0723 | 0.49111 | 0.021 | 0.06 | 10 | 12.5 | 1 | [9]
FS | 10001 | 50000 | 0.2 | [7 empty] | 0.0482 | 0.32741 | 0.018 | 0.05 | 7.5 | 10 | 1 | [9]
FS | 50001 | 1000000 | 0.1 | [7 empty] | 0.0241 | 0.1637 | 0.015 | 0.04 | 5 | 7.5 | 1 | [9]
BFS | 0 | 2000 | 0.4 | [7 empty] | 0.0964 | 0.65482 | 0.025 | 0.077 | 13.75 | 16.5 | 30 | Estimación a partir del coste del FS de [9]
BFS | 2001 | 10000 | 0.3 | [7 empty] | 0.0723 | 0.49111 | 0.021 | 0.066 | 11 | 13.75 | 30 | Estimación a partir del coste del FS de [9]
BFS | 10001 | 50000 | 0.2 | [7 empty] | 0.0482 | 0.32741 | 0.018 | 0.055 | 8.25 | 11 | 30 | Estimación a partir del coste del FS de [9]
BFS | 50001 | 1000000 | 0.1 | [7 empty] | 0.0241 | 0.1637 | 0.015 | 0.044 | 5.5 | 8.25 | 30 | Estimación a partir del coste del FS de [9]
CAB | 0 | 2000 | 0.4 | [6 empty] | 30 | 0.15381 | 0.94423 | 0.025 | 0.32 | 412.5 | 605 | 30 | Estimación a partir del coste de [41]
CAB | 2001 | 10000 | 0.3 | [6 empty] | 30 | 0.12971 | 0.78052 | 0.021 | 0.26 | 275 | 412.5 | 30 | Estimación a partir del coste de [41]
CAB | 10001 | 50000 | 0.2 | [6 empty] | 30 | 0.10561 | 0.61682 | 0.018 | 0.189 | 192.5 | 275 | 30 | Estimación a partir del coste de [41]
CAB | 50001 | 1000000 | 0.1 | [6 empty] | 30 | 0.08151 | 0.45311 | 0.015 | 0.132 | 165 | 192.5 | 30 | Estimación a partir del coste de [41]
FQ-D | 0 | 2000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.019 | 0.066 | 9.5 | 14 | 1 | [41]
FQ-D | 2001 | 10000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.017 | 0.066 | 7.7 | 13.4 | 1 | [41]
FQ-D | 10001 | 50000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.014 | 0.056 | 4.9 | 7.7 | 1 | [41]
FQ-D | 50001 | 1000000 | 0.02 | 56.5 |  |  | 5.3 |  |  |  | 0.049161 | 0.62183 | 0.012 | 0.054 | 4.9 | 5.1 | 1 | [41]
EDI | 0 | 2000 | 1.5 |  |  |  |  | 0.0003 |  |  | 0.3615 | 2.4556 | 0.095 | 0.4 | 350 | 400 | 1 | [9]
EDI | 2001 | 10000 | 1.3 |  |  |  |  | 0.0003 |  |  | 0.3133 | 2.1282 | 0.082 | 0.3 | 300 | 350 | 1 | [9]
EDI | 10001 | 50000 | 1.1 |  |  |  |  | 0.0003 |  |  | 0.2651 | 1.8007 | 0.07 | 0.25 | 225 | 300 | 1 | [9]
EDI | 50001 | 1000000 | 0.8 |  |  |  |  | 0.0003 |  |  | 0.1928 | 1.3096 | 0.065 | 0.2 | 200 | 225 | 1 | [9]
CAP/CAG | 0 | 2000 | 0.4 | [6 empty] | 30 | 0.15381 | 0.94423 | 0.025 | 0.32 | 375 | 550 | 1 | [41]
CAP/CAG | 2001 | 10000 | 0.3 | [6 empty] | 30 | 0.12971 | 0.78052 | 0.021 | 0.26 | 250 | 375 | 1 | [41]
CAP/CAG | 10001 | 50000 | 0.2 | [6 empty] | 30 | 0.10561 | 0.61682 | 0.018 | 0.189 | 175 | 250 | 1 | [41]
CAP/CAG | 50001 | 1000000 | 0.1 | [6 empty] | 30 | 0.08151 | 0.45311 | 0.015 | 0.132 | 150 | 175 | 1 | [41]
POA | 0 | 2000 | 0.75 | [5 empty] | 9.9 |  | 0.19264 | 1.2858 | 0.068 | 0.6 | 250 | 300 | 0 | [41][42]
POA | 2001 | 10000 | 0.5 | [5 empty] | 9.9 |  | 0.13239 | 0.8765 | 0.059 | 0.5 | 200 | 225 | 0 | [41][42]
POA | 10001 | 50000 | 0.3 | [5 empty] | 9.9 |  | 0.08419 | 0.54909 | 0.051 | 0.45 | 150 | 175 | 0 | [41][42]
POA | 50001 | 1000000 | 0.17 | [5 empty] | 9.9 |  | 0.05286 | 0.33628 | 0.0422 | 0.4 | 100 | 135 | 0 | [41][42]
DES | 0 | 2000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0015 | 0.002 | 12.5 | 15 | 0 | [9]
DES | 2001 | 10000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0013 | 0.002 | 10 | 12.5 | 0 | [9]
DES | 10001 | 50000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.0011 | 0.001 | 7.5 | 10 | 0 | [9]
DES | 50001 | 1000000 | 0.005 | [7 empty] | 0.001205 | 0.0081852 | 0.00093 | 0.001 | 5 | 7.5 | 0 | [9]
BRM | 0 | 2000 | 1.2 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.39972 | 9.208 | 0.9 | 1.1 | 3000 | 1600 | 30 | [47]
BRM | 2001 | 10000 | 0.7 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.27922 | 8.3895 | 0.6 | 0.5 | 1600 | 1000 | 30 | [47] | EN COLUMNES I, J… I SUCCESSIVEDS ES PODEN AFEGIR MÉS CARACT. (P.E. impacte (subproductes, consum reactius, emissió GEH, olor/soroll), flexibilitat, robustesa, necessitat personal qualificat), alguns d'ells poden ser qualitatius p.e. SI/NO, o Baix/Mitjà/Alt
BRM | 10001 | 50000 | 0.6 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.25512 | 8.2258 | 0.5 | 0.4 | 1000 | 800 | 30 | [47]
BRM | 50001 | 1000000 | 0.55 | 80 | 1.9 | 17.1 | 4.5 |  |  |  | 0.24307 | 8.1439 | 0.4 | 0.2 | 800 | 600 | 30 | [47]
UF | 0 | 2000 | 0.6 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.17285 | 3.4751 | 0.069 | 0.85 | 1400 | 1800 | 0 | [41]. LIFE WIRE
UF | 2001 | 10000 | 0.5 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.14875 | 3.3113 | 0.063 | 0.56 | 800 | 1400 | 0 | [41]. LIFE WIRE
UF | 10001 | 50000 | 0.3 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.10055 | 2.9839 | 0.054 | 0.32 | 450 | 800 | 0 | [41]. LIFE WIRE
UF | 50001 | 1000000 | 0.1 |  | 1.2 | 6.3 | 3.2 |  |  |  | 0.05235 | 2.6565 | 0.045 | 0.13 | 350 | 450 | 0 | [41]. LIFE WIRE
OI | 0 | 2000 | 3.5 |  |  |  | 0.8 | 0.0003 |  |  | 0.84527 | 5.7523 | 0.092 | 0.24 | 500 | 650 | 1 | [41]. LIFE WIRE
OI | 2001 | 10000 | 2 |  |  |  | 0.8 | 0.0003 |  |  | 0.48377 | 3.2967 | 0.081 | 0.2 | 350 | 500 | 1 | [41]. LIFE WIRE
OI | 10001 | 50000 | 1.5 |  |  |  | 0.8 | 0.0003 |  |  | 0.36327 | 2.4782 | 0.069 | 0.18 | 275 | 350 | 1 | [41]. LIFE WIRE
OI | 50001 | 1000000 | 1 |  |  |  | 0.8 | 0.0003 |  |  | 0.24277 | 1.6597 | 0.055 | 0.17 | 250 | 275 | 1 | [41]. LIFE WIRE

## Impactes ambientals
| Unitats | kg CO2 eq./un. | L eq. / un. | Font | Procés
Consum electricitat | kWh | 0.241 | 1.637 | Empremta carboni: OCCC, 2020, Guia Pràctica per al càlcul d'emissions de gasos amb efecte d'hivernacle (GEH). Març 2020; Empremta hídrica: Ecoinvent v3.5
FeCl3 | kg | 0.57741 | 7.7683 | Ecoinvent v3.5 (2018) | 1 kg Iron (III) chloride, without water, in 40% solution state {CH}¦ iron (III) chloride production, product in 40% solution state ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
NaOCl | kg | 2.2809 | 18.8242 | Ecoinvent v3.5 (2018) | 1 kg Sodium hypochlorite, without water, in 15% solution state {RER}¦ sodium hypochlorite production, product in 15% solution state ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
Citric acid | kg | 2.9268 | 377.709 | Ecoinvent v3.5 (2018) | 1 kg Citric acid {RER}¦ production ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
NaOH | kg | 1.1054 | 14.1679 | Ecoinvent v3.5 (2018) | 1 kg Sodium hydroxide, 50% in H2O, production mix, at plant/RER S (of project Ecoinvent system processes)
HCl | kg | 0.96217 | 9.0947 | Ecoinvent v3.5 (2018) | 1 kg Hydrochloric acid, without water, in 30% solution state {RER}¦ hydrochloric acid production, from the reaction of hydrogen with chlorine ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
H2O2 | kg | 1.201 | 5.8569 | Ecoinvent v3.5 (2018) | 1 kg Hydrogen peroxide, without water, in 50% solution state {RER}¦ hydrogen peroxide production, product in 50% solution state ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
Carbó actiu (verge) | kg | 8.0409 | 26.3947 | Ecoinvent v3.5 (2018) | 1 kg Activated carbon, granular {RER}¦ activated carbon production, granular from hard coal ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)
Carbó actiu (regeneració) | kg | 0.8324 | 6.6915 | Ecoinvent v3.5 (2018) | 1 kg Activated carbon, granular {RER}¦ treatment of spent activated carbon, granular from hard coal, reactivation ¦ APOS, S (of project Ecoinvent 3 - allocation at point of substitution - system)

## Abrev
BFS | Biofiltre de sorra
BRM | Bioreactor de membrana
CAB | Carbo activat biologic
Cl | Cloro
ClO2 | Dioxido de cloro
COT | Carbo organic total
DEET | N,N-diethyl-m-toluamide
DES | Desinfecció
DP | Decantacio primaria
DS | Decantacio secundaria
EDI | Electrodialisis inversa
FeCl3 | Clorur ferric
FQ-D | Fisicoquimic+Decantacio
FS | Filtracio per sorra
GAC | Carbo activat granular
H2O2 | Peroxid d'hidrogen
HCL | Acid cloridric
MF/UF | Microfiltracio/ultrafiltracio
MON | Material organic natural
N.A | No aplica
N.E | No especifica
NaClO | Hipoclorito de sodio
NaOH | Hidroxid de sodi
NDMA | N-nitrosodimethylamine
NH4+ | Amoni
Ni | Niquel
NO3- | Nitrat
O3 | Ozono
OI | Osmosis inversa
PAC | Carbo activat en pols
PFOS | Acid sulfonic-perfluorooctane
pH | Potencial d'hidrogen
POA | Procesos oxidacio avançada
SST | Solids totals en suspensió
UV | Ultraviolat
Zn | Zinc

## REF
[1] | J. Yang, M. Monnot, L. Ercolei, and P. Moulin, “[1],” Membranes (Basel)., vol. 10, no. 6, pp. 1–56, 2020, doi: 10.3390/membranes10060131.
[2] | L. Katz, K. Kinney, U. Civil, and J. Simpson, “Pilot Scale Test of a Water-Treatment System for Initial Removal of Organic Compounds,” vol. 836, 2008.
[3] | S. Di Fabio, S. Lampis, L. Zanetti, F. Cecchi, and F. Fatone, “Role and characteristics of problematic biofilms within the removal and mobility of trace metals in a pilot-scale membrane bioreactor,” Process Biochem., vol. 48, no. 11, pp. 1757–1766, 2013, doi: 10.1016/j.procbio.2013.08.005.
[4] | K. Kümmerer, Di. D. DIonysiou, and D. Fatta-Kassinos, Scope of the Book Advanced Treatment Technologies for Urban Wastewater Reuse, vol. 45. 2016.
[5] | C. Echevarría et al., “[5],” Sci. Total Environ., vol. 671, pp. 288–298, 2019, doi: 10.1016/j.scitotenv.2019.03.365.
[6] | S. California, R. B. Management, and L. C. Region, “Secondary / Emerging Constituents Report,” no. October, 2009.
[7] | D. S. Francy et al., “Comparative effectiveness of membrane bioreactors, conventional secondary treatment, and chlorine and UV disinfection to remove microorganisms from municipal wastewaters,” Water Res., vol. 46, no. 13, pp. 4164–4178, 2012, doi: 10.1016/j.watres.2012.04.044.
[8] | J. Ottoson, A. Hansen, B. Björlenius, H. Norder, and T. A. Stenström, “Removal of viruses, parasitic protozoa and microbial indicators in conventional and membrane processes in a wastewater pilot plant,” Water Res., vol. 40, no. 7, pp. 1449–1457, 2006, doi: 10.1016/j.watres.2006.01.039.
[9] | Raquel Iglesias Esteban, “LA REUTILIZACIÓN DE EFLUENTES DEPURADOS EN ESPAÑA: RETROSPECTIVA, DESARROLLO DEL MARCO NORMATIVO, ESTUDIO DE LAS TECNOLOGÍAS DE REGENERACIÓN FRENTE A LOS BIORREACTORES DE MEMBRANA Y SUS COSTES EN FUNCIÓN DEL USO,” UNIVERSIDAD POLITÉCNICA DE MADRID, 2016.
[10] | H. D. S. Metcalf & Eddy Inc, George Tchobanoglous, Franklin L Burton, Wastewater Engineering Treatment & Reuse, 4th edició. 2014.
[11] | C. Sheng, A. G. A. Nnanna, Y. Liu, and J. D. Vargo, “[11],” Sci. Total Environ., vol. 550, pp. 1075–1083, 2016, doi: 10.1016/j.scitotenv.2016.01.179.
[12] | S. Merel and S. A. Snyder, “[12],” Environ. Int., vol. 96, pp. 98–117, 2016, doi: 10.1016/j.envint.2016.09.004.
[13] | M. W. LeChevallier, “Water Treatment and Pathogen Control: Process Efficiency in Achieving Safe Drinking-water,” Water Intell. Online, vol. 12, 2013, doi: 10.2166/9781780405858.
[14] | Bratby J., “Coagulation and Flocculation in Water and wastewater Treatment.,” IWA PUBLISHING, 2006. .
[15] | R. G. Saseendran and K. Swarnalatha, “Removal of Zinc from Industrial Wastewater Using Cork Powder as Adsorbent,” no. Ii, pp. 11–15, 2016.
[16] | P. O. Box and U. A. Emirates, “Removal of Cadmium , Copper , Lead and Nickel from Aqueous Solution by White , Yellow and Red United Arab Emirates Sand L . Pappalardo , F . Jumean and N . Abdo Department of Biology and Chemistry , American University of Sharjah ,” Filtration, vol. 6, no. 3, pp. 41–44, 2010.
[17] | I. X. and B. J., “[17],” Water Treat., 2013, doi: 10.5772/50481.
[18] | M. Bourgin et al., “Evaluation of a full-scale wastewater treatment plant upgraded with ozonation and biological post-treatments: Abatement of micropollutants, formation of transformation products and oxidation by-products,” Water Res., vol. 129, pp. 486–498, 2018, doi: 10.1016/j.watres.2017.10.036.
[19] | L. Rizzo, A. Fiorentino, M. Grassi, D. Attanasio, and M. Guida, “[19],” J. Environ. Chem. Eng., vol. 3, no. 1, pp. 122–128, 2015, doi: 10.1016/j.jece.2014.11.011.
[20] | J. W. Hatt, E. Germain, and S. J. Judd, “Granular activated carbon for removal of organic matter and turbidity from secondary wastewater,” pp. 846–854, 2013, doi: 10.2156/wst.2012.644.
[21] | S. Kumar et al., “Low ‑ cost activated carbon production from organic waste and its utilization for wastewater treatment,” Appl. Water Sci., vol. 10, no. 2, pp. 1–9, 2020, doi: 10.1007/s13201-020-1145-z.
[22] | M. W. Luca Sbardella, Joaquim Comas, Alessio Fenu, Ignasi ROdriguez-Roda, “[22],” Sci. Total Environ., vol. 636, pp. 519–529, 2018.
[23] | A. K. Meena, C. Rajagopal, and D. Organisation, “Removal of heavy metal ions from aqueous solutions using chemically ( Na 2 S ) treated granular activated carbon as an adsorbent,” no. June, 2010.
[24] | P. R. Compendium, “Potable Reuse Compendium,” 2017.
[25] | World Health Organisation, [25]. 2017.
[26] | B. Garmen, “Investigating the Efficacy of Sodium Hypochlorite, Calcium Hypochlorite and Peracetic Acid on Environmental Eschericia Coli Strains,” Stellenbosch Univ. Carmen thesis, no. 1, pp. 1–133, 2015.
[27] | Q. Lin et al., “Sanitizing agents for virus inactivation and disinfection,” View, vol. 1, no. 2, 2020, doi: 10.1002/viw2.16.
[28] | and M. J. A. Laura J. Rose, Eugene W. Rice, Lisa Hodges, Alicia Peterson, “Monochloramine Inactivation of Bacterial Select Agents,” Appl Env. Microbiol, vol. 73, 2007.
[29] | I. Health, R. Figures, and T. Table, “Chapter 7 Virological Compliance,” no. October 2005, pp. 1–25, 2019.
[30] | R. W. Herschy, “Water quality for drinking: WHO guidelines,” Encycl. Earth Sci. Ser., pp. 876–883, 2012, doi: 10.1007/978-1-4020-4410-6_184.
[31] | H. J. van der F.-K. J L Banach, L S van Overbeek, M N Nierop Groot, P S van der Zouwen, “Efficacy of chlorine dioxide on Escherichia coli inactivation during pilot-scale fresh-cut lettuce processing,” Int J Food Microbiol, vol. 269, 2018.
[32] | M. W. Lechevallier and K.-K. Au, “3.1 Factors Affecting Disinfection,” WHO Water Treat. Pathog. Control Process Effic. Achiev. Safe Drink. Water, pp. 41–65, 2004.
[33] | L. Rizzo et al., “Science of the Total Environment [33],” Sci. Total Environ., vol. 710, p. 136312, 2020, doi: 10.1016/j.scitotenv.2019.136312.
[34] | M. P. Del Pino and B. Durham, “Wastewater reuse through dual-membrane processes: Opportunities for sustainable water resources,” Desalination, vol. 124, no. 1–3, pp. 271–277, 1999, doi: 10.1016/S0011-9164(99)00112-5.
[35] | K. J. Godri et al., “Science of the Total Environment 1 , 4-Dioxane as an emerging water contaminant : State of the science and evaluation of research needs,” Sci. Total Environ., vol. 690, no. June, pp. 853–866, 2019, doi: 10.1016/j.scitotenv.2019.06.443.
[36] | M. Antônio and S. Rodrigues, Electrodialysis and Water Reuse. 2014.
[37] | L. Rizzo et al., “Science of the Total Environment [37],” vol. 655, no. October 2018, pp. 986–1008, 2019, doi: 10.1016/j.scitotenv.2018.11.265.
[38] | Y. Ahn, D. Cho, A. N. Kabra, M. Ji, and Y. Yoon, “Removal of Iopromide and Its Intermediates from Ozone-Treated Water Using [38],” no. September, pp. 0–9, 2015, doi: 10.1007/s11270-015-2594-0.
[39] | C. P. James, E. Germain, and S. Judd, “Micropollutant removal by advanced oxidation microfiltered secondary effluent for water reuse of Abstract,” vol. 127, no. April, pp. 77–83, 2014.
[40] | A. Matos, M. Gmurek, and R. M. Quinta-ferreira, “Ozone and Photocatalytic Processes for Pathogens Removal from Water : A Review,” pp. 1–23, doi: 10.3390/catal9010046.
[41] | W. Science, T. Guo, J. D. Englehardt, and T. Wu, “[41] : Water and wastewater treatment and reuse processes Water Science and Technology [41] : Water and Wastewater Treatment and Reuse Processes,” no. January, 2014, doi: 10.2166/wst.2013.734.
[42] | U. von G. Ioannis A. Katsoyiannis, Silvio Canonica, “[42].,” Water Res., vol. 45, no. 12, pp. 3811–3822, 2011.
[43] | J. Mamo, M. J. García-galán, M. Stefani, S. Rodríguez-mozaz, and D. Barceló, “[43],” Chem. Eng. J., vol. 331, no. June 2017, pp. 450–461, 2018, doi: 10.1016/j.cej.2017.08.050.
[44] | R. Sharma, Sanjay K., Sanghi, Wastewater Reuse and Management. Springer Netherlands, 2013.
[45] | E. O. Ezugbe and S. Rathilal, “Membrane technologies in wastewater treatment: A review,” Membranes (Basel)., vol. 10, no. 5, 2020, doi: 10.3390/membranes10050089.
[46] | P. R. B. A. Chin, “[46],” Water Res., vol. 39, no. 10, pp. 2136–2144, 2005.
[47] | Z. Z. Ping Li, Li Liu, Jiaojiao Wu, Rong Cheng, Lei Shi, Xiang Zheng, “Identify driving forces of MBR applications in China,” Sci. Total Environ., vol. 647, pp. 627–638, 2019.
[48] | F. Pontius, “Regulation of Perfluorooctanoic Acid ( PFOA ) and Perfluorooctane Sulfonic Acid ( PFOS ) in Drinking Water : A Comprehensive Review,” 2019.
[49] | M. Zolfaghari, P. Drogui, B. Seyhi, S. K. Brar, G. Buelna, and R. Dubé, “Occurrence, fate and effects of di (2-ethylhexyl) phthalate in wastewater treatment plants: A review,” Environ. Pollut., vol. 194, pp. 281–293, 2014, doi: 10.1016/j.envpol.2014.07.014.
[50] | V. A. Arias Espana, M. Mallavarapu, and R. Naidu, “Treatment technologies for aqueous perfluorooctanesulfonate (PFOS) and perfluorooctanoate (PFOA): A critical review with an emphasis on field testing,” Environ. Technol. Innov., vol. 4, no. May, pp. 168–181, 2015, doi: 10.1016/j.eti.2015.06.001.
[51] | membrane bioreactor and electrochemical advanced oxidation process: Kinetic study and toxicity assessment,” Chemosphere, vol. 193, pp. 160–169, 2018, doi: 10.1016/j.chemosphere.2017.11.010.
[52] | H. K. Jakopovic, M. Matošic, and I. Mijatovic, “Treatment of food industry wastewaters in membrane bioreactor,” Proc. - 2008 Jt. Cent. Eur. Congr. 4th Cent. Eur. Congr. Food, CEFood 2008 6th Croat. Congr. Food Technol. Biotechnol. Nutr., vol. 1, no. October, pp. 177–188, 2008.
[53] | T. K. Kim, T. Kim, W. S. Choe, M. K. Kim, Y. J. Jung, and K. D. Zoh, “Removal of heavy metals in electroplating wastewater by powdered activated carbon (PAC) and sodium diethyldithiocarbamate-modified PAC,” Environ. Eng. Res., vol. 23, no. 3, pp. 301–308, 2018, doi: 10.4491/eer.2017.208.
[54] | Lionel Ho, Gayle Newcombe, 2005, Effect of NOM, turbidity and floc size on the PAC adsorption of MIB during alum coagulation